## NVPC (26)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Machine Part Room
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620239
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 9040 |  | 585 | Pass
| L-02 |  | 7440 |  | 422 | Pass
| Average |  | 8240 |  | 504
| STD |  | 1131 |  | 115
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (25)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Garment Wash Area
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620238
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 14803 |  | 757 | Pass
| L-02 |  | 9220 |  | 437 | Pass
| L-03 |  | 6989 |  | 322 | Pass
| L-04 |  | 14398 |  | 945 | Pass
| Average |  | 11352 |  | 615
| STD |  | 3863 |  | 287
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (24)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Bung Process Airlock
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620237
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 15756 |  | 760 | Pass
| L-02 |  | 11932 |  | 587 | Pass
| L-03 |  | 15421 |  | 901 | Pass
| L-04 |  | 21085 |  | 1207 | Pass
| L-05 |  | 25499 |  | 1487 | Pass
| L-06 |  | 34809 |  | 2185 | Pass
| L-07 |  | 25694 |  | 1525 | Pass
| L-08 |  | 15450 |  | 831 | Pass
| L-09 |  | 16825 |  | 1022 | Pass
| L-10 |  | 20865 |  | 1262 | Pass
| Average |  | 20334 |  | 1177
| STD |  | 6812 |  | 469
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (23)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Bung Washing Airlock
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620236
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 15615 |  | 751 | Pass
| L-02 |  | 16881 |  | 897 | Pass
| Average |  | 16248 |  | 824
| STD |  | 895 |  | 103
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (22)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Washing Corridor
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620235
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 25430 |  | 1188 | Pass
| L-02 |  | 24516 |  | 1329 | Pass
| L-03 |  | 24020 |  | 1264 | Pass
| L-04 |  | 21950 |  | 1105 | Pass
| L-05 |  | 21549 |  | 1150 | Pass
| Average |  | 23493 |  | 1207
| STD |  | 1676 |  | 90
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (21)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Blending Corridor
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202346
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-03 | L-01 |  | 150 |  | 18 | Pass
| L-02 |  | 191 |  | 19 | Pass
| L-03 |  | 105 |  | 12 | Pass
| L-04 |  | 164 |  | 14 | Pass
| Average |  | 152 |  | 16
| STD |  | 36 |  | 3
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE B |  |  | 3520 |  |  | 29
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (20)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Cool Zone
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202345
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-03 | L-01 |  | 154 |  | 10 | Pass
| L-02 |  | 184 |  | 19 | Pass
| L-03 |  | 154 |  | 9 | Pass
| L-04 |  | 235 |  | 15 | Pass
| L-05 |  | 224 |  | 12 | Pass
| L-06 |  | 163 |  | 12 | Pass
| Average |  | 186 |  | 13
| STD |  | 36 |  | 4
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE B |  |  | 3520 |  |  | 29
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (19)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Sterile Corridor
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202344
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-03 | L-01 |  | 215 |  | 16 | Pass
| L-02 |  | 290 |  | 14 | Pass
| L-03 |  | 183 |  | 14 | Pass
| L-04 |  | 216 |  | 14 | Pass
| L-05 |  | 199 |  | 20 | Pass
| L-06 |  | 166 |  | 22 | Pass
| Average |  | 212 |  | 17
| STD |  | 43 |  | 4
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE B |  |  | 3520 |  |  | 29
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (18)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-III (SA)
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202343
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-03 | L-01 |  | 288 |  | 8 | Pass
| L-07 |  | 289 |  | 17 | Pass
| Average |  | 288 |  | 12
| STD |  | 1 |  | 6
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE B |  |  | 3520 |  |  | 29
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (17)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-II (SA)
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202342
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-03 | L-01 |  | 17270 |  | 1634 | Pass
| L-07 |  | 13777 |  | 1703 | Pass
| Average |  | 15524 |  | 1668
| STD |  | 2470 |  | 49
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (16)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-I & Exit-II (SA)
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202341
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-02 | L-01 |  | 37914 |  | 7474 | Pass
| L-07 |  | 43560 |  | 6931 | Pass
| Average |  | 40737 |  | 7202
| STD |  | 3992 |  | 384
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE D |  |  | 3520000 |  |  | 29000
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (15)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Bung Washing & Sterilization
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202340
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 19436 |  | 1908 | Pass
| L-02 |  | 14971 |  | 1562 | Pass
| L-03 |  | 20160 |  | 1817 | Pass
| L-04 |  | 19116 |  | 1888 | Pass
| L-05 |  | 19099 |  | 1502 | Pass
| L-06 |  | 14491 |  | 1033 | Pass
| L-07 |  | 16893 |  | 2014 | Pass
| L-08 |  | 15503 |  | 1461 | Pass
| L-09 |  | 14369 |  | 1070 | Pass
| L-10 |  | 12653 |  | 778 | Pass
| Average |  | 16669 |  | 1503
| STD |  | 2629 |  | 423
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (14)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Washing Corridor
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620234
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 25430 |  | 1188 | Pass
| L-02 |  | 24516 |  | 1329 | Pass
| L-03 |  | 24020 |  | 1264 | Pass
| Average |  | 24655 |  | 1260
| STD |  | 715 |  | 71
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (13)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Rubber Bung & Al. Seal Day Store
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202339
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 11613 |  | 795 | Pass
| L-02 |  | 16341 |  | 2214 | Pass
| Average |  | 13977 |  | 1504
| STD |  | 3343 |  | 1003
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (12)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Garment Wash
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202338
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 13163 |  | 1562 | Pass
| L-02 |  | 15466 |  | 1739 | Pass
| Average |  | 14314 |  | 1650
| STD |  | 1628 |  | 125
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (11)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Vial Washing Room
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202337
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 19257 |  | 1662 | Pass
| L-02 |  | 19108 |  | 1526 | Pass
| L-03 |  | 16422 |  | 1546 | Pass
| L-04 |  | 17562 |  | 1551 | Pass
| L-05 |  | 20591 |  | 2309 | Pass
| L-06 |  | 13070 |  | 1528 | Pass
| L-07 |  | 14463 |  | 1544 | Pass
| L-08 |  | 10576 |  | 1601 | Pass
| L-09 |  | 9873 |  | 1520 | Pass
| Average |  | 15658 |  | 1643
| STD |  | 3886 |  | 254
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (10)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Vial Washing Corridor
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202336
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 8096 |  | 566 | Pass
| L-02 |  | 7424 |  | 487 | Pass
| L-03 |  | 10875 |  | 1016 | Pass
| L-04 |  | 14734 |  | 1499 | Pass
| Average |  | 10282 |  | 892
| STD |  | 3323 |  | 467
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (9)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-III & Exit-I (NS)
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202335
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 14749 |  | 1406 | Pass
| L-02 |  | 12584 |  | 1159 | Pass
| L-03 |  | 14857 |  | 1642 | Pass
| Average |  | 14063 |  | 1402
| STD |  | 1282 |  | 242
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (8)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-II (NS)
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202334
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 23850 |  | 2523 | Pass
| L-02 |  | 17176 |  | 2219 | Pass
| Average |  | 20513 |  | 2371
| STD |  | 4719 |  | 215
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (7)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-I & Exit-II (NS)
LOCATION |  | CEPHA BLOCK
REPORT NO. |  | PPE027PC1506202333
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-08 | L-01 |  | 111576 |  | 9392 | Pass
| L-02 |  | 51290 |  | 10100 | Pass
| L-03 |  | 99944 |  | 10634 | Pass
| Average |  | 87603 |  | 10042
| STD |  | 31982 |  | 623
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE D |  |  | 3520000 |  |  | 29000
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 20/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (6)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-III & Exit-I
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620233
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45A | L-01 |  | 16400 |  | 862 | Pass
| L-02 |  | 25912 |  | 1499 | Pass
| L-03 |  | 33141 |  | 1757 | Pass
| Average |  | 25151 |  | 1373
| STD |  | 8396 |  | 461
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (5)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-II
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620232
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45A | L-01 |  | 16859 |  | 980 | Pass
| L-02 |  | 22275 |  | 1310 | Pass
| Average |  | 19567 |  | 1145
| STD |  | 3830 |  | 233
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (4)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Outer Corridor
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC1506202312
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-44 | L-01 |  | 83563 |  | 10955 | Pass
| L-02 |  | 31583 |  | 4861 | Pass
| L-03 |  | 52148 |  | 9649 | Pass
| L-04 |  | 52440 |  | 9392 | Pass
| L-05 |  | 37146 |  | 6980 | Pass
| L-06 |  | 46118 |  | 12519 | Pass
| L-07 |  | 57053 |  | 8720 | Pass
| L-08 |  | 43512 |  | 3576 | Pass
| L-09 |  | 57398 |  | 7115 | Pass
| L-10 |  | 63520 |  | 6614 | Pass
| L-11 |  | 77030 |  | 6408 | Pass
| L-12 |  | 85920 |  | 14332 | Pass
| L-13 |  | 71306 |  | 6647 | Pass
| L-14 |  | 98016 |  | 8277 | Pass
| L-15 |  | 73434 |  | 5436 | Pass
| L-16 |  | 92587 |  | 8111 | Pass
| Average |  | 63923 |  | 8100
| STD |  | 20045 |  | 2810
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE D |  |  | 3520000 |  |  | 29000
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (3)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Vial Washing & Sterilization
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC1506202311
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 10074 |  | 706 | Pass
| L-02 |  | 8519 |  | 499 | Pass
| L-03 |  | 8826 |  | 538 | Pass
| L-04 |  | 9448 |  | 581 | Pass
| L-05 |  | 11938 |  | 771 | Pass
| L-06 |  | 13550 |  | 885 | Pass
| L-07 |  | 11473 |  | 763 | Pass
| L-08 |  | 10549 |  | 620 | Pass
| L-09 |  | 9678 |  | 557 | Pass
| Average |  | 10451 |  | 658
| STD |  | 1620 |  | 130
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC (2)
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | Vial Washing Entry Airlock
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC1506202310
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45 | L-01 |  | 9669 |  | 603 | Pass
| L-02 |  | 11172 |  | 589 | Pass
| Average |  | 10420 |  | 596
| STD |  | 1063 |  | 10
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE C |  |  | 352000 |  |  | 2900
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd

## NVPC
PARTICLE COUNT TEST
CUSTOMER NAME |  | VHB Medisciences Ltd
ADDRESS |  | Plot No 20-22 & 49-51, IIE, Sector-5, SIDCUL, Pantnagar-263145, UTTARAKHAND
TEST TAKEN ON |  | 15/06/2023
TEST TAKEN CONDITION |  | At Rest
AHU NO. |  | CH-I & Exit-II
LOCATION |  | GENERAL BLOCK(Dry)
REPORT NO. |  | PPE027PC150620231
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME | MAKE/MODEL |  |  | SR.NO. |  |  | VALIDITY
Particle Counter | 3920 |  |  | 950147 |  |  | 10/04/2024
OBSERVATIONS:
Room Name | Location |  | ≥ 0.5 μm |  | ≥ 5.0 μm | Remarks
AHU-45A | L-01 |  | 97495 |  | 9542 | Pass
| L-02 |  | 41786 |  | 7171 | Pass
| L-03 |  | 71972 |  | 10090 | Pass
| Average |  | 70418 |  | 8934
| STD |  | 27887 |  | 1551
Maximum Permitted number of particles/m³ equal to or greater than the tabulated size as per EU:GMP ISO:2015
GRADE |  |  | 0.5 μ m |  |  | 5.0 μm
GRADE D |  |  | 3520000 |  |  | 29000
TEST PREPARED OUT BY |  |  | VERIFIED BY
Electronically Signed by Prince temp on 16/06/2023
PIN POINT ENGINEERS |  |  | VHB Medisciences Ltd