## AV-new
PAO REPORT
CUSTOMER NAME |  |  | Pin Point Engineers
ADDRESS |  |  | Dehradun
TEST TAKEN ON |  |  | 29/05/2023
REGENT USED |  |  | PAO
AHU NUMBER |  |  | 1
LOCATION |  |  | : XYZ
REPORT NO. |  |  | PPE003PAO290520231
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  | SR.NO. |  | VALIDITY
Photometer |  | PH-5 |  |  | 2829 |  | 16/01/2024
OBSERVATIONS:
Room Name | Inlet No. |  | Upstream Conc (μg/l) |  | Leakage Found (%) | Remark
Gr | f1 |  | 67 |  | 0.0012 | Pass
Compressed Air Pressure 1.5 kg/cm²
Acceptance criteria :Leakage should not be more Than 0.01 %
REPORT PREPARED BY |  |  |  | VERIFIED BY
Electronically Signed by Anukriti Sharma on 29/05/2023
PIN POINT ENGINEERS |  |  |  | Pin Point Engineers