## AV-new
AIR VELOCITY REPORT
CUSTOMER NAME |  |  | Pin Point Engineers
ADDRESS |  |  | Dehradun
TEST TAKEN ON |  |  | 22/05/2023
AHU NO. |  |  | 10
DEPARTMENT |  |  | ds
REPORT NO. |  |  | PPE003AV2205202310
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  |  | SR.NO. |  |  |  | VALIDITY
Anemometer |  | AVM-04 |  |  |  | S12K240201 |  |  |  | 25/03/2023
OBSERVATIONS:
Room Name | Inlet No. |  | V1 | V2 | V3 | V4 | V5 | Avg. Vel. | Inlet Size Ft2 | CFM | Room Volume (Ft3) | ACPH
| A-01/S-01 |  | 90 | 80 | 110 | 80 | 100 | 92 | 4 | 368 | 1000 | 70.08
| A-01/S-02 |  | 150 | 120 | 140 | 130 | 110 | 130 | 4 | 520
| A-01/S-03 |  | 90 | 70 | 60 | 70 | 60 | 70 | 4 | 280
TOTAL CFM | [9 empty] | 1168
Acceptance criteria :Not less Than 45 ACPH | [6 empty] | GRADE : C
REPORT PREPARED BY |  |  |  |  | VERIFIED BY
Electronically Signed by temp user on 22/05/2023
PIN POINT ENGINEERS |  |  |  |  | Pin Point Engineers