## AV-new
AIR VELOCITY REPORT
CUSTOMER NAME |  |  | Pin Point Engineers
ADDRESS |  |  | Dehradun
TEST TAKEN ON |  |  | 22/05/2023
EQUIPMENT ID |  |  | fg
DEPARTMENT |  |  | hggf
REPORT NO. |  |  | PPE003AV220520237
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  |  | SR.NO. |  |  | VALIDITY
Anemometer |  | AVM-04 |  |  |  | S12K240201 |  |  | 25/03/2023
OBSERVATIONS:
Equipment Name | Inlet No. | V1 |  | V2 |  | V3 |  | V4 | V5 | AVERAGE VELOCITY (FPM)
fg | df | 90 |  | 110 |  | 100 |  | 80 | 90 | 94
| df | 90 |  | 110 |  | 80 |  | 90 | 70 | 88
| df | 100 |  | 110 |  | 150 |  | 80 | 90 | 106
Acceptance criteria : NMT 90± 20 % ( 72 TO 108 FPM) | [6 empty] | GRADE : A
REPORT PREPARED BY |  |  |  |  | VERIFIED BY
Electronically Signed by temp user on 22/05/2023
PIN POINT ENGINEERS |  |  |  |  | Pin Point Engineers