## AV-new
PAO REPORT
CUSTOMER NAME |  |  | Pin Point Engineers
ADDRESS |  |  | Dehradun
TEST TAKEN ON |  |  | 22/05/2023
AHU NO/EQUIPMENT ID |  |  | AHU-10
LOCATION |  |  | saa
REPORT NO. |  |  | PPE003PAO220520231
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  | SR.NO. |  | VALIDITY
Photometer |  | PH-5 |  |  | 3690 |  | 28/03/2023
OBSERVATIONS:
Room Name/ /Equipment Name | Inlet No. |  | Upstream Conc (μg/l) |  | Leakage Found (%) | Remark
| ss |  | 25 |  | 0.0045 | Pass
| s1 |  | 37 |  | 0.0043 | Pass
Compressed Air Pressure 1.5 kg/cm²
Acceptance criteria :Leakage should not be more Than 0.03 %
REPORT PREPARED BY |  |  |  | VERIFIED BY
Electronically Signed by temp user on 22/05/2023
PIN POINT ENGINEERS |  |  |  | Pin Point Engineers